## METER5
PROJECT NAME : | 1519 Geneva St |  |  |  |  | CITY OF AURORA UTILITY DEPARTMENT |  |  |  | ¦ | FAX TO :____________________________________ DATE :__________
[6 empty] | 1470 SOUTH HAVANA STR., AURORA, CO. 80012 |  |  |  | ¦
PROJECT ADDRESS : | 1519 Geneva St |  |  |  |  | TAP APPLICATION OFFICE - 739-7395 |  |  |  | ¦ | ATTEN. :________________________________ FAX # :____________
[6 empty] | PLANS REVIEW - 739-7374 FAX - 739-7491 |  |  |  | ¦
| EXISTING WATER SAVING FIXTURES ? |  |  |  |  | NO | PROPOSED WATER SAVING FIXTURES ? |  |  |  | yes |  | DATE : |  | BY : |  | OK BY :
FIXTURE UNIT TABLE | EXISTING ULTRA LOW FLOW FIXTURE? |  |  |  |  | NO | PROPOSED ULTRA LOW FLOW FIXTURE? |  |  |  | yes
| EXISTING PRIVATE |  |  |  | PROPOSED PRIVATE |  | EXISTING PUBLIC |  | PROPOSED PUBLIC |  |  |  | STANDARD |  | LOW FLOW |  | ULTRA LOW FLOW
| NUMBER OF |  | FIXTURE |  | NUMBER OF | FIXTURE | NUMBER OF | FIXTURE | NUMBER OF |  | FIXTURE | UNITS
FIXTURE | FIXTURES |  | VALUE |  | FIXTURES | VALUE | FIXTURES | VALUE | FIXTURES |  | VALUE | SUBTOTALS | PRIV | PUB | PRIV | PUB | PRIV | PUB
BAR SINK |  |  | 1 |  |  | 0.7 |  | 2 |  |  | 1.4 | 0 | 1 | 2 | 0.7 | 1.4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
BATHTUB (WITH SHOWER) |  |  | 2 |  |  | 1.4 |  | 4 |  |  | 1.8 | 0 | 2 | 4 | 1.4 | 1.8
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
DENTAL UNIT |  |  | 1 |  |  | 0.7 |  | 1 |  |  | 0.7 | 0 | 1 | 1 | 0.7 | 0.7
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
DRINKING FOUNTAIN |  |  | 1 |  |  | 0.7 |  | 2 | 2 |  | 1.4 | 2.8 | 1 | 2 | 0.7 | 1.4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
HOSE BIBB OR SILL COCK |  |  | 3 |  | 1 | 3 |  | 5 |  |  | 5 | 3 | 3 | 5 | 3 | 5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
MOBILE HOME EACH |  |  | 6 |  |  | 6 |  | 6 |  |  | 6 | 0 | 6 | 6 | 6 | 6
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
LAUNDRY TUB, CLOTHWASHER |  |  | 2 |  |  | 2 |  | 4 |  |  | 4 | 0 | 2 | 4 | 2 | 4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
LAVATORY |  |  | 1 |  |  | 0.7 |  | 2 | 2 |  | 1.4 | 2.8 | 1 | 2 | 0.7 | 1.4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
LAVATORY (DENTAL) |  |  | 1 |  |  | 0.7 |  | 1 |  |  | 0.7 | 0 | 1 | 1 | 0.7 | 0.7
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
LAWN SPRINKLER EACH HEAD |  |  | 1 |  |  | 1 |  | 1 |  |  | 1 | 0 | 1 | 1 | 1 | 1
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
SHOWER EACH HEAD |  |  | 2 |  |  | 1.4 |  | 4 |  |  | 2.8 | 0 | 2 | 4 | 1.4 | 2.8
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
SINK (PER FAUCET) |  |  | 1 |  |  | 0.7 |  | 2 | 1 |  | 1.4 | 1.4 | 1 | 2 | 0.7 | 1.4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
SINK DISHWASHER |  |  | 2 |  |  | 1.4 |  | 4 |  |  | 2.8 | 0 | 2 | 4 | 1.4 | 2.8
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
SINK (FLUSHING RIM) |  |  | 10 |  |  | 7 |  | 10 |  |  | 7 | 0 | 10 | 10 | 7 | 7
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
SINK (WASHUP) |  |  | 2 |  |  | 1.4 |  | 2 | 1 |  | 1.4 | 1.4 | 2 | 2 | 1.4 | 1.4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
SINK (CIRCULAR WASHUP) |  |  | 4 |  |  | 2.8 |  | 4 |  |  | 2.8 | 0 | 4 | 4 | 2.8 | 2.8
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
URINAL (PEDESTAL) |  |  | 10 |  |  | 5 |  | 10 |  |  | 5 | 0 | 10 | 10 |  |  | 5 | 5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
URINAL (STALL) |  |  | 5 |  |  | 2.5 |  | 5 |  |  | 2.5 | 0 | 5 | 5 |  |  | 2.5 | 2.5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
URINAL (WALL) |  |  | 5 |  |  | 2.5 |  | 5 |  |  | 2.5 | 0 | 5 | 5 |  |  | 2.5 | 2.5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
URINAL (FLUSH TANK) |  |  | 3 |  |  | 1.5 |  | 3 |  |  | 2.5 | 0 | 3 | 3 |  |  | 1.5 | 2.5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
WATER CLOSET (TANK) |  |  | 3 |  |  | 1.5 |  | 5 | 2 |  | 2.5 | 5 | 3 | 5 | 2.4 | 3.5 | 1.5 | 2.5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
WATER CLOSET (VALVE) |  |  | 6 |  |  | 3 |  | 10 |  |  | 5 | 0 | 6 | 10 | 4.7 | 7 | 3 | 5
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
3/8 INCH SUPPLY |  |  | 1 |  |  | 1 |  | 2 |  |  | 2 | 0 | 1 | 2
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
1/2 INCH SUPPLY |  |  | 2 |  |  | 2 |  | 4 |  |  | 4 | 0 | 2 | 4
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
3/4 INCH SUPPLY |  |  | 3 |  |  | 3 |  | 6 |  |  | 6 | 0 | 3 | 6
- | - |  | - |  | - | - | - | - | - |  | - | - | - | - | - | - | - | -
1 INCH SUPPLY |  |  | 6 |  |  | 6 |  | 10 |  |  | 10 | 0 | 6 | 10
[11 empty] | TOTAL | 16.4 |  |  | MAXIMUM
* IF WATER SAVING AND/OR ULTRA LOW FLOW FIXTURE VALUES ARE USED THEY MUST BE SPECIFIED ON | [14 empty] | FIXTURE
THE BUILDING PLANS PRIOR TO APPROVAL OF THE BUILDING PERMIT. | [14 empty] | UNITS
WATER SAVINGS = 30% REDUCTION ON FAUCETS & 3.5 GALLON WATER CLOSETS
ULTRA LOW FLOW = 1.6 GALLON WATER CLOSETS AND URINALS | [14 empty] | FLUSH | FLUSH
[15 empty] | TANK | VALVE
METER SIZING TABLE | [5 empty] | HEAD LOSS CALCULATIONS BASE ON HAZEN WILLIAMS COEFFICIENT | [6 empty] | METER | MAX. | CURVE | CURVE
CURVE NO. 1 FOR FLUSH VALVES | [5 empty] | COPPER SERVICE C = 130, DUCTILE IRON C = 100 | [6 empty] | SIZE | FLOW | # | #
CURVE NO. 2 FOR FLUSH TANKS |  | CURVE NO. |  | = | 2 | HAZEN WILLIAMS C = |  | 130 |  |  |  |  | DIA. | (GPM) | 2 | 1
| FIXTURE |  | FLOW FROM |  | METER | VELOCITY | LENGTH | HEAD | STATIC |  | PRESSURE |  | 3/4" | 14 | 20 | -
| UNIT |  | TABLE |  | SIZE |  | SERVICE | LOSS | PRESSURE |  | @ BLDG. |  | 1" | 25 | 41 | 9
| TOTAL |  | (GPM) |  | (INCHES) | (FPS) | (FT) | PSI/100FT | @ MAIN |  | (PSI) |  | 1 1/2" | 55 | 150 | 60
[13 empty] | 2" | 100 | 375 | 246
[13 empty] | 3" | 220 | 1075 | 1075
| 16.4 |  | 11.84 |  | 0.75 | 8.6993 | 50 | 22.5116 | 90 |  | 78.7442 |  | 4" | 400 | 2675 | 2675
[13 empty] | 6" | 900 | 5500 | 5500
[30 empty] | fixture units | flow | flow
[31 empty] | for flush | for flush
[31 empty] | valve | tank
[27 empty] | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | 0 | 0 | 0 | 5 | 20 | 4
[27 empty] | 0 | 0 | 0 | 10 | 27 | 7
[27 empty] | 1 | 32.84 | 11.84 | 15 | 32 | 11
[27 empty] | 0 | 0 | 0 | 20 | 35 | 14
[27 empty] | 0 | 0 | 0 | 25 | 37 | 16
[27 empty] | 0 | 0 | 0 | 30 | 42 | 19
[27 empty] | 0 | 0 | 0 | 35 | 44 | 22
[27 empty] | 0 | 0 | 0 | 40 | 46 | 24
[27 empty] | 0 | 0 | 0 | 45 | 48 | 26
[27 empty] | 0 | 0 | 0 | 50 | 51 | 28
[27 empty] | 0 | 0 | 0 | 55 | 53 | 30
[27 empty] | 0 | 0 | 0 | 60 | 55 | 32
[27 empty] | 0 | 0 | 0 | 65 | 57 | 34
[27 empty] | 0 | 0 | 0 | 70 | 58 | 36
[27 empty] | 0 | 0 | 0 | 75 | 60 | 37
[27 empty] | 0 | 0 | 0 | 80 | 61 | 38
[27 empty] | 0 | 0 | 0 | 85 | 63 | 39
[27 empty] | 0 | 0 | 0 | 90 | 65 | 41
[27 empty] | 0 | 0 | 0 | 95 | 67 | 42
[27 empty] | 0 | 0 | 0 | 100 | 68 | 43
[27 empty] | 0 | 0 | 0 | 105 | 69 | 45
[27 empty] | 0 | 0 | 0 | 110 | 70 | 46
[27 empty] | 0 | 0 | 0 | 115 | 71 | 47
[27 empty] | 0 | 0 | 0 | 120 | 72 | 48
[27 empty] | 0 | 0 | 0 | 125 | 74 | 49
[27 empty] | 0 | 0 | 0 | 130 | 75 | 50
[27 empty] | 0 | 0 | 0 | 135 | 76 | 52
[27 empty] | 0 | 0 | 0 | 140 | 77 | 53
[27 empty] | 0 | 0 | 0 | 145 | 78 | 54
[27 empty] | 0 | 0 | 0 | 150 | 80 | 55
[27 empty] | 0 | 0 | 0 | 155 | 81 | 56
[27 empty] | 0 | 0 | 0 | 160 | 82 | 57
[27 empty] | 0 | 0 | 0 | 165 | 83 | 58
[27 empty] | 0 | 0 | 0 | 170 | 86 | 59
[27 empty] | 0 | 0 | 0 | 175 | 87 | 60
[27 empty] | 0 | 0 | 0 | 180 | 88 | 61
[27 empty] | 0 | 0 | 0 | 190 | 89 | 62
[27 empty] | 0 | 0 | 0 | 195 | 90 | 64
[27 empty] | 0 | 0 | 0 | 200 | 91 | 65
[27 empty] | 0 | 0 | 0 | 205 | 92 | 66
[27 empty] | 0 | 0 | 0 | 210 | 93 | 67
[27 empty] | 0 | 0 | 0 | 215 | 94 | 68
[27 empty] | 0 | 0 | 0 | 220 | 95 | 69
[27 empty] | 0 | 0 | 0 | 225 | 96 | 70
[27 empty] | 0 | 0 | 0 | 230 | 97 | 71
[26 empty] | MAXIUM | 0 | 0 | 0 | 235 | 98 | 72
[26 empty] | FLOW | 0 | 0 | 0 | 240 | 99 | 73
[26 empty] | ALLOWED | 0 | 0 | 0 | 245 | 100 | 74
[19 empty] | DIA. | TYPE K CU | DIP |  |  |  |  | (GPM) | 0 | 0 | 0 | 250 | 101 | 75
[19 empty] | 3/4" | 0.745 |  | 0.75 | 1 | 0.745 | 0.75 | 14 | 0 | 0 | 0 | 300 | 110 | 85
[19 empty] | 1" | 0.995 |  | 1 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 350 | 120 | 95
[19 empty] | 1 1/2" | 1.481 |  | 1.5 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 400 | 128 | 105
[19 empty] | 2" | 1.959 |  | 2 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 450 | 134 | 112
[19 empty] | 3" |  | 3.4 | 3 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 500 | 141 | 122
[19 empty] | 4" |  | 4.22 | 4 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 550 | 149 | 132
[19 empty] | 6" |  | 6.28 | 6 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 600 | 157 | 142
[24 empty] | 0.745 | 0.75 |  | 0 | 0 | 0 | 650 | 132 | 151
[27 empty] | 0 | 0 | 0 | 700 | 170 | 160
[27 empty] | 0 | 0 | 0 | 750 | 178 | 170
[27 empty] | 0 | 0 | 0 | 800 | 183 | 179
[27 empty] | 0 | 0 | 0 | 850 | 189 | 188
[27 empty] | 0 | 0 | 0 | 900 | 197 | 195
[27 empty] | 0 | 0 | 0 | 950 | 202 | 201
[27 empty] | 0 | 0 | 0 | 1000 | 209 | 209
[27 empty] | 0 | 0 | 0 | 1050 | 215 | 215
[27 empty] | 0 | 0 | 0 | 1100 | 220 | 220
[27 empty] | 0 | 0 | 0 | 1150 | 225 | 225
[27 empty] | 0 | 0 | 0 | 1200 | 231 | 231
[27 empty] | 0 | 0 | 0 | 1250 | 240 | 240
[27 empty] | 0 | 0 | 0 | 1300 | 248 | 248
[27 empty] | 0 | 0 | 0 | 1350 | 253 | 253
[27 empty] | 0 | 0 | 0 | 1400 | 258 | 258
[27 empty] | 0 | 0 | 0 | 1450 | 263 | 263
[27 empty] | 0 | 0 | 0 | 1500 | 270 | 270
[27 empty] | 0 | 0 | 0 | 1550 | 277 | 277
[27 empty] | 0 | 0 | 0 | 1600 | 284 | 284
[27 empty] | 0 | 0 | 0 | 1650 | 291 | 291
[27 empty] | 0 | 0 | 0 | 1700 | 298 | 298
[27 empty] | 0 | 0 | 0 | 1800 | 308 | 308
[27 empty] | 0 | 0 | 0 | 1900 | 318 | 318
[27 empty] | 0 | 0 | 0 | 2000 | 328 | 328
[27 empty] | 0 | 0 | 0 | 2100 | 348 | 348
[27 empty] | 0 | 0 | 0 | 2200 | 351 | 351
[27 empty] | 0 | 0 | 0 | 2300 | 361 | 361
[27 empty] | 0 | 0 | 0 | 2400 | 372 | 372
[27 empty] | 0 | 0 | 0 | 2500 | 382 | 382
[27 empty] | 0 | 0 | 0 | 2600 | 393 | 393
[27 empty] | 0 | 0 | 0 | 2700 | 403 | 403
[27 empty] | 0 | 0 | 0 | 2800 | 412 | 412
[27 empty] | 0 | 0 | 0 | 2900 | 423 | 423
[27 empty] | 0 | 0 | 0 | 3000 | 435 | 435
[27 empty] | 0 | 0 | 0 | 3500 | 500 | 500
[27 empty] | 0 | 0 | 0 | 4000 | 600 | 600
[27 empty] | 0 | 0 | 0 | 4500 | 700 | 700
[27 empty] | 0 | 0 | 0 | 5000 | 800 | 800
[27 empty] | 0 | 0 | 0 | 5500 | 900 | 900
[28 empty] | 32.84 | 11.84